## 1-START HERE-Instructions
User Guide v1.0
Downstream Defender® Sizing Calculator for Kansas City MARC Manual
Introduction
1. Please Read These Instructions.
Thank you for downloading the Downstream Defender Sizing Calculator for Kansas City area projects being designed in accordance with the MARC Manual.
We hope this will be a useful tool for engineers who would like a simple and convenient way to to determine the required Downstream Defender model size
for a given site. With a few basic User Inputs, the calculator will recommend a Downstream Defender model size that meets the MARC Manaul treatment
objectives. It will generate a "NOT FOR CONSTRUCTION" General Arrangement Drawing and provide a Downstream Defender specification for use on
your project.
An online Downstream Defender Sizing Calculator can provide more detailed drawings but you will need to use flow information from this spreadsheet.
http://www.hydro-int.com/us/products/downstream-defender
Future updates of the online tool will incorporate the APWA MARC design process.
Please contact Hydro International at (207) 756-6200 or email at any point during the process if you require assistance. |  |  |  | stormwaterinquiry@hydro-int.com
Basis of Design.
The APWA MARC Manual 2012 sets out guidelines for the use of various stormwater BMPs, the design standard and assigns a Value Rating (VR)
to each for a total VR for the site. The VR is used to determine complicance with the requirements of the regulations.
Table 4.5 stipulates the VR that are assigned to the BMP for control of various SW pollutants.
The Downstream Defender can have a VR for TSS and Oils / Floatables. For TSS control the effluent concentration must be controlled to prescribed maximum
concentraions for corresponding VR. The Higher the VR the lower the allowable effluent level. The manual does not detail how the effluent concentration is
calculated therefore an independendtly verifed industry standard has been used for this design process. A full test report is avaiable on request.
By controlling the flow through the Downstream Defender the effluent level can be controlled. This design sheet allows the designer to control how much
water is directed to the unit to allow control of the effluent level to obtain the desired VR for TSS.
Oils and Floatables are significantly controlled bythe Downstream Defender. This is proven in both lab and field studies.
These reports are available on request and a VR of 2 is recommended.
Using the Downstream Defender Sizing Calculator
2. Determine the Downstream Defender model size needed for your project. On the "Step 2 - Sizing Tab":
STEP 1 - Enter Project Information.
STEP 2 - Calculate a Water Quality Flow Rate.
STEP 3 - Define the Value Ratings (VRs) based on MARC Manual criteria.
STEP 4 - Enter the Peak Storm information and Invert Elevation of the Storm Drain Pipe at the proposed Downstream Defender location.
Also Enter proposed Rim or Finished Grade elevation of the Downstream Defender.
PRINT Worksheet "2-Sizing" to use as a general Downstream Defender specification for your project.
3. Obtain a General Arrangement drawing. Using the Calaculator's recommended size, proceed to the "Step 3a-Get Online GA Dwg" Worksheet. Or, proceed instead to the "Step 3b-Get Offline GA Dwg" Worksheet if the project requires an external bypass/junction manhole.
4. If you need a written Downstream Defender specification for a project, proceed to the "Step 4-Get Specification" Worksheet.
Click on the hyperlink and download the latest specification document from our website (internet connection required).
5. Submit your outputs to Hydro International. |  |  | Go to http://ci25.actonsoftware.com/acton/form/2795/0001:d-0001/1/index.htm to submit your
design for a complimentary technical review and price estimate.
Subsititutes - "Or Approved Equal"
The use of an effluent control standard makes the assessment of the "equal" more difficult. The APWA MARC rules require the treatment of a fixed WQ flow rate at which the effluent must be controlled to a prescribed maximum. This means that any alternate to the Downstream Defender must demonstrate the same level of effluent control of the same particle size (OK110). The differential between inlet and outlet, known as Total Suspended Solids (TSS) reduction can not be used as a basis of comparison. For example 80% TSS is based on the difference between inlet and out concentrations but may exceed the effluent control level required. Therefore TSS reduction levels can not be used as a basis of comparison.
Any substitue, if allowed, must show equal effluent control at the WQ flow using OK110 test sand or finer using independently verified lab data. This is addressed in our supporting specification which can be downloaded here:
DOWNLOAD LINK
NEED HELP? If you need help at any time, please visit our Help Form to submit a question and a Hydro International technical expert will reply within
8 business hours. Or call our Stormwater Product Specialists at (207) 321-3750 from 8 AM - 5 PM EST.
Help form at: http://ci25.actonsoftware.com/acton/form/2795/000e:d-0001/1/index.htm

## 2-Sizing
[10 empty] | 2013-01-01 | 41275
[7 empty] | Today's Date: | 2012-08-12 |  | Date | 41133 | 2
| STEP 1. Enter Project and Contact Information in YELLOW Cells | [8 empty] | 2.1 WQF Units | 1
[10 empty] | 2.1 WQF | 0 | 0
| Project Name: |  |  | Contact Name: | [5 empty] | 2.2 Sizing Methodology | 10 | 1
| Location: |  |  | Company:
| Application: |  |  | Phone: | [6 empty] | Determine Size
| Development Type: | New Development |  | E-mail: | [5 empty] | Max. WQF = 19.973132594523 cfs | 0 | 19.9731
| STEP 2. Water Quality Flow Calculation Rational Method |  |  | STEP 3. Define "Value Rating" (VR) from Section 4.0 of APWA MARC Manual
| as prescribed in the APWA MARC Manual Section 6.4. Edit YELLOW cells. |  |  | Enter values in YELLOW cells.
| Water Quality Flow Rational Method: Q=KCiA |  |  |  | Enter Water Quality Flow Required for VR Score: |  | cfs
| Drainage Area (ac): |  |  |  | Input Water Quality VR Required:
| Time of Concentraion, tc, (min): |  |  |  | Corresponding Max Effluent Concentration : | 50 | mg/L
| Runoff Coefficient ( c ): |  |  |  | Oils & Floatables VR:
| Intensity (i), looks up value from MARC Manual Table 6.3) |  | 1.68 |  | The Total VR Score: | 2
Antecedent Precipitation (K):
| Water Quility Flow (Q): |  | 0 | STEP 4. Enter Project's Design Flow Rates and Site Information
[7 empty] | Invert Elev of Storm Drain Pipe = |  | -ft. |  |  |  | Model Number & Diameter | Peak Hydraulic Flow in Online Arrangement (cfs) | Maximum Pipe Diameter (in) | Headloss at Peak Treatment Flow (in) | Oil Storage Capacity (gal) | Sediment Storage Capacity (cu-yd) | Min Dist. From Outlet Invert to Top of Rim (ft) | Standard Dist. From Sump Floor to Outlet Invert (ft)
| Select Method: | Regulatory Agency |  | Peak Flow Rate = |  | cfs | Pipe Diameter of Storm Drain Pipe = |  | -in. | Recommended Unit |  |  | --- | --- | --- | --- | --- | --- | --- | ---
Drop-down list for sizing method
| Regulatory Agency: | Target Particle Size: |  | Peak Flow Storm Frequency = |  | year | Rim Elevation = |  | -ft. | Regulatory Agency | 1
| MARC | 50-micron | [7 empty] | Target Particle Size | 2 |  |  | Drop-down List for Applications |  |  | Drop-down List for Application Types
[10 empty] | Selected Method | 1 |  |  | Pre-treatment |  |  | Re-development
[10 empty] | Selected TPS | 2 |  |  | Primary Treatment |  |  | New Development
Sizing Recommendation and Design Parameters
| 1 | Vortex Chamber Diameter
| 2 | Maximum Inlet Pipe Diameter | [7 empty] | Drop-down list for sizing criteria |  |  | Drop-down list for target particel size |  |  |  | Error for Rim to Invert
| 3 | Oil Storage Capacity | [8 empty] | Other | 1 |  | 110-micron | 1 |  | #VALUE!
| 4 | Sediment Storage Capacity | [8 empty] | New Jersey DEP | 2 |  | 50-micron | 2 |  | ***Warning***
| 5 | Outlet Pipe Diameter | [8 empty] | Maine DEP | 3 |  |  |  |  | Min. Rim El. =
| 6 | Minimum Stormdrain Depth (Final Grade to Outlet Invert) | [8 empty] | Washington DOE | 4
| 7 | Standard Depth - Outlet Invert to Sump | [8 empty] | City of Indianapolis | 5
[11 empty] | City of Fort Wayne | 6
[11 empty] | St. Louis MSD | 7
94 Hutchins Drive, Portland, Maine 04102 t:(207) 756-6200 f:(207) 756-6212 www.hydro-int.com | [10 empty] | City of Nashville | 8
[11 empty] | New York DEC | 9
[11 empty] | MARC | 10
[11 empty] | Hydraulic Design Check |  | #VALUE!
[11 empty] | Tolerance= |  | 10% | 110% | #VALUE! |  | Dia | 4 | 6 | 8 | 10 | 12
[11 empty] | ***Hydraulic Capacity Warning*** Off-line System Required Peak Flow Rate > Model's Peak Treatmnt Flow Rate Proceed with "Off-line" Design Step 4b | ***Hydraulic Capacity Check*** No Bypass Required Proceed with "On-Line" Design - Step4a | ***ERROR*** WQF exceeds available sizing. Press HELP to request technical support. |  |  | Freq | PTFR | 3 | 8 | 15 | 25 | 38 | Tol Value
[16 empty] | <10 | Tolerance1 | 3.5 | 8.5 | 15.5 | 25.5 | 38.5 | #N/A
[16 empty] | >10 | Tolerance2 | 4 | 9 | 17 | 28 | 42 | #N/A
[11 empty] | ***Pipe Diameter Warning*** Off-line System Required Stormdrain pipe dia. > Model's Max. Inlet Pipe dia. Proceed with "Off-line" Design - Step 4b | ***Off-line System Required*** City of Indianapolis requires all systems to be Off-Line. Proceed with Offline Design- Step 4b |  |  |  | SD & Hydraulic Checks:
SD Pipe Dia Check
If SD Pipe Dia. <= Max. Inlet Pipe Dia. Then Online
[16 empty] | If Freq > 10-yr then infrequent |  |  |  | frequent
[16 empty] | Recommendation |  |  |  | offline
[15 empty] | Bypass Note - |  | Note: Bypass Required
City of Indianapolis
Downstream Defender®
Sizing Calculator For Kansas City MARC Manual
Click to Submit Your Design for a Price Estimate and a Complimentary Technical Review
Diameter Downstream Defender
Min. Depth =
Depth - Outlet Invert to Sump =
--
--
--
--
--
--
--
--
--
--
--
Note: Bypass Required
--

## Flow Rate Charts (hidden)
Unit Diameter | Outside New Jersey Treatment Flow Rates1 | NJDEP Flow Rate2 | MEDEP Flow Rates3 | Indianapolis Flow Rates3 | Fort Wayne Flow Rates8 | Wash DOE Flow Rates4 | St. Louis MSD Flow Rates5 | Nashville Flow Rates7 | 50-Micron Flow Rates | 50-Micron Flow Rates Metric Units | MARC
Removal Efficiency Rating | 80% TSS Removal | 50% TSS Removal | 60% TSS Removal | 80% TSS Removal | 80% TSS Removal | 80% TSS Removal | 80% TSS Removal | 50% TSS Removal | 80% TSS Removal6 | 80% TSS Removal6
(feet) | (cfs) | cfs | cfs | cfs | cfs | cfs | cfs | cfs | cfs | lps
4 | 1.56 | 1.12 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 3 | 1.22 | 34.526
6 | 4.2989 | 2.52 | 3.58 | 3.58 | 4.1 | 4.1 | 4.1 | 8 | 3.3619 | 95.1425
8 | 8.8247 | 4.48 | 7.35 | 7.35 | 9.4 | 9.4 | 9.4 | 15 | 6.9014 | 195.3085
10 | 15.4161 | 7 | 12.85 | 12.85 | 17.7 | 17.7 | 17.7 | 25 | 12.0562 | 341.19
12 | 24.318 | 10.08 | 20.27 | -- | -- | -- | -- | -- | 19.0179 | 538.2071
Scaling N-value | 2.5 | 2 | 2.5 | 2.5 | 2.85 | 2.85 | 2.85 | 2.5 | 2.5 | 2.5
1. Determined by performance testing using OK-110 test sediment.
These flow rates and 80% efficiency are usedin jurisdictions where no other criteria is specified. | [12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
2.Based on performance testing using F-95 test sediment, Indirect testing. See NJCAT Tech Verification Report | [12 empty] | Other | New Jersey DEP | Maine DEP | Washington DOE | City of Indianapolis | City of Fort Wayne | St. Louis MSD | City of Nashville | New York DEC | MARC
3. Based on Jeff Dennis witnessed report for 583 gpm on July 12, 2002 | [8 empty] | WQF= | 0 |  | 4 | 1.56 | 1.12 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 3 | 1.12 | 1.2813
4. Same as MEDEP | [8 empty] | Sizing Method# | 10 |  | 6 | 4.3 | 2.52 | 3.58 | 4.1 | 3.58 | 4.1 | 4.1 | 8 | 2.52 | 3.5308
5. Based on MEDEP witnessed-testing with scaling factor of 2.85 | [11 empty] | 8 | 8.82 | 4.48 | 7.35 | 9.4 | 7.35 | 9.4 | 9.4 | 15 | 4.48 | 7.248
6. Based on 50-micron performance testing and 2.5 scaling | [11 empty] | 10 | 15.42 | 7 | 12.85 | 17.7 | 12.85 | 17.7 | 17.7 | 25 | 7 | 12.6617
Calgory also requires | [11 empty] | 12 | 24.32 | 10.08 | 20.27 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 10.08 | 19.9731
7. Used peak flow rates listed as MTFR | [10 empty] | Max |  | 24.32 | 10.08 | 20.27 | 17.7 | 12.85 | 17.7 | 17.7 | 25 | 10.08
8. Based on previous City of Indianapolis 2.85 scaling factor, that was downgraded to 2.5. Fort Wayne stil 2.85 | [10 empty] | Flow for user input sizing method -Reg Agency |  | 4: Flow for user input sizing method-TPS=110; 8: Flow for user input sizing method-TPS=50
[11 empty] | 4 | 1.2813 | 4: 4; 5: 1.56; 8: 4; 9: 1.22
[11 empty] | 6 | 3.5308 | 4: 6; 5: 4.3; 8: 6; 9: 3.3619
[11 empty] | 8 | 7.248 | 4: 8; 5: 8.82; 8: 8; 9: 6.9014
[11 empty] | 10 | 12.6617 | 4: 10; 5: 15.42; 8: 10; 9: 12.0562
[11 empty] | 12 | 19.9731 | 4: 12; 5: 24.32; 8: 12; 9: 19.0179
[11 empty] | Model Size = |  | 1: 4; 4: Model Size=; 5: 4; 8: Model Size=; 9: 4
[9 empty] | Selected Method |  | 1 |  | 1: Agency; 2: 4
[9 empty] | Selected TPS |  | 2 |  | 1: TPS100; 2: 4
[13 empty] | TPS50 | 4
[11 empty] | Model= | 4
[11 empty] | MAX. WQF= | 19.9731

## 3a-Get Online GA Dwg
Dia |  | -ft. | --
Outlet Pipe Dia | #N/A | -in. | -- | #N/A | #N/A
MTFR | #N/A | -cfs | --
PTFR | #N/A | -cfs | --
Headloss | #N/A | -ft. | --
Sed Storage | #N/A | -gal. | --
Oil Storage | #N/A | -gal. | --
Min. Depth | #N/A | -ft. | -- | --
Std Sump Depth | #N/A | -ft | -- | --
Notes: | 1. THIS IS A STANDARD DETAIL AND IS NOT SITE SPECIFIC. ACTUAL INLET PIPE DIAMETER AND ANGLE MAY BE DIFFERENT THAN SHOWN.
2. REFER TO SUBMITTAL OR FABRICATION DRAWINGS FOR FINAL RIM AND INVERT ELEVATIONS. NOTE: INLET INVERT IS ONE PIPE DIAMETER LOWER THAN THE OUTLET INVERT.
3. CONTACT HYDRO INTERNATIONAL FOR SITE SPECIFIC DRAWINGS AND INSTALLATION REQUIREMENTS.
Rim El.= | 0 | --
Oultet Pipe I.E= | 0 | -- | --
Invert Pipe I.E.= | #N/A | --
Sump El.= | #N/A | --
Depth= | 0 | --
--
--
--
--
--
--
--
--
--
DO NOT USE FOR CONSTRUCTION OR FABRICATION
1. THIS IS A STANDARD DETAIL AND IS NOT SITE SPECIFIC. ACTUAL INLET PIPE DIAMETER AND ANGLE MAY BE DIFFERENT THAN SHOWN.
2. REFER TO SUBMITTAL OR FABRICATION DRAWINGS FOR FINAL RIM AND INVERT ELEVATIONS. NOTE: INLET INVERT IS ONE PIPE DIAMETER LOWER THAN THE OUTLET INVERT.
3. CONTACT HYDRO INTERNATIONAL FOR SITE SPECIFIC DRAWINGS AND INSTALLATION REQUIREMENTS.
8/12/2012
#N/A
#N/A
--
--
--
--
--
--
#N/A
--
--

## 3b-Get Offline GA Dwg
Dia |  | -ft. | --
Outlet Pipe Dia | #N/A | " | -- | Max. -- | -- STORMDRAIN | in. | -- | OUTLET PIPE
MTFR | #N/A | -cfs | -- |  | -- SD OUTLET
PTFR | #N/A | -cfs | -- |  | MAX. -- SD
Headloss | #N/A | -ft. | -- |  | MAX. -- STORMDRAIN
Sed Storage | #N/A | -gal. | -- |  | INLET PIPE
Oil Storage | #N/A | -gal. | --
Min. Depth | #N/A | -ft. | -- | --
Std Sump Depth | #N/A | -ft | -- | --
Notes: | 1. THIS IS A STANDARD DETAIL AND IS NOT SITE SPECIFIC. ACTUAL INLET PIPE DIAMETER AND ANGLE MAY BE DIFFERENT THAN SHOWN.
2. REFER TO SUBMITTAL OR FABRICATION DRAWINGS FOR FINAL RIM AND INVERT ELEVATIONS. NOTE: INLET INVERT IS ONE PIPE DIAMETER LOWER THAN THE OUTLET INVERT.
3. CONTACT HYDRO INTERNATIONAL FOR SITE SPECIFIC DRAWINGS AND INSTALLATION REQUIREMENTS.
Rim El.= | 0 | --
Oultet Pipe I.E= | 0 | --
Invert Pipe I.E.= | #N/A | --
Sump El.= | #N/A | --
Depth= | 0 | --
--
--
--
--
--
--
--
--
--
--
DO NOT USE FOR CONSTRUCTION OR FABRICATION
1. THIS IS A STANDARD DETAIL AND IS NOT SITE SPECIFIC. ACTUAL INLET PIPE DIAMETER AND ANGLE MAY BE DIFFERENT THAN SHOWN.
2. REFER TO SUBMITTAL OR FABRICATION DRAWINGS FOR FINAL RIM AND INVERT ELEVATIONS. NOTE: INLET INVERT IS ONE PIPE DIAMETER LOWER THAN THE OUTLET INVERT.
3. CONTACT HYDRO INTERNATIONAL FOR SITE SPECIFIC DRAWINGS AND INSTALLATION REQUIREMENTS.
8/12/2012
-- SD OUTLET
INLET PIPE
--
--
--
--
--
--
MAX. -- STORMDRAIN
-- STORMDRAIN
OUTLET PIPE
INLET PIPE
MAX. -- SD
INV EL.=

## MARC Table (hidden)
Water Quality Flow Calculation Rational Method
as prescribed in the APWA MARC Manual Section 6.4
Water Quality Flow Rational Method: Q=KCiA
Drainage Area (ac): | 0
Time of Concentraion (tc): | 0
Runoff Coefficient ( c ): | 0
Intensity (i):
Antecedent Precipitation (K): | 0 | (Set at 1 for Water Quality Storm which is 90% Event)
Water Quility Flow (Q):
Downstream Defender Sizing to achieve Value Rating (VR)
Section 4.0 of APWA MARC Manual
Enter Water Quality Flow Required for VR Score: | 0 | cfs
Input Water Quality VR Required: | 0 | (Enter value 1,2,3 or 4)
Corresponding Max Effluent Concentration : |  | mg/l
Oils & Floatables VR: | 2 | (Set 1 or 2; The Downstream Defender has significant Oils and Floatables capture = 2)
The Total VR Score:
Select the smallest unit that meets the water treatment goal.
Note that the peak flow may require the unit to be installed offline.
Downstream Defender Size ( Dia ft) | Q for VR
4 | 1.2813 | cfs | OK
6 | 3.5308 | cfs | OK
8 | 7.248 | cfs | OK
10 | 12.6617 | cfs | OK
12 | 19.9731 | cfs | OK

## Step 3-Get Specification (hidden)
Double Click on Word Box to Edit Specification | PG 1 | PG 2 | PG 3 | PG 4 | PG 5

## Specification Text (hidden)
Get Downstream Defender Specification | [5 empty] | Hydrodynamic Vortex Separator Performance Specifications
Click to Download a Word *.doc Copy of the Downstream Defender Specification online. | [5 empty] | Dia | Max Depth1 | MTFR-502 | MTFR-1002 | Scour Flow Rate3 | PTFR4 | Headloss5 | Oil Storage Capacity6 | Sediment Storage Capacity6
OR | [5 empty] | (feet) | (feet) | (cfs) | (cfs) | (cfs) | (cfs) | (feet) | (gal.) | (gal.)
Enable Your Macros and click the "Copy to Word" button below to generate a Word file. NOTE: You must be running Microsoft Office 2007 or later for this option to work. | [5 empty] | 4 | 4.1 | 1.2 | 1.6 | 2.4 | 3 | 0.68 | 70 | 141
| PG 1 | PG 2 | PG 3 | PG 4 | PG 5 | 6 | 5.9 | 3.4 | 4.3 | 6.5 | 8 | 0.95 | 216 | 424
[6 empty] | 8 | 7.7 | 6.9 | 8.8 | 13.3 | 15 | 1.1 | 540 | 939
[6 empty] | 10 | 9.4 | 12 | 15 | 23.3 | 25 | 1.2 | 1050 | 1757
PART 1 - GENERAL | [5 empty] | 12 | 11.2 | 19 | 24 | 38 | 38 | 1.4 | 1770 | 2970
1.01 SCOPE
A. Work described in this section includes furnishing all labor, equipment, materials, tools and incidentals required for a complete and operable installation of the Hydrodynamic Vortex Separator (HVS) stormwater treatment system as shown on the drawings and specified herein.
B. The manufacturer shall design and supply the equipment listed herein and the Contractor shall install the equipment in accordance with the manufacturer’s Handling, Storage, and Installation Instructions.
1.02 GENERAL REQUIREMENTS
A. The HVS shall use an induced vortex to separate pollutants from stormwater runoff. The system shall be self-activating with no mechanical parts or external power requirements.
B. Upon request, independently certified performance data and references shall be made available to the Engineer of Record for use in determining that the HVS meets the design criteria and performance requirements stated herein.
1.03 SUBMITTALS
A. Submittals shall be provided and shall include the following:
i. Site plan showing location and orientation of proposed pipe sizes, connections and excavation limits.
ii. Product installation drawings showing plan and elevation views with water elevations for the flow conditions specified herein.
iii. Performance data as required in Part 2.
iv. Inspection and maintenance procedures with accompanying maintenance video and upon request, three references for verifying successful completion of the maintenance procedures and associated costs.
1.04 QUALITY ASSURANCE
A. The HVS shall be manufactured under the direction of an ISO 9001 Certified Company.
B. Inspection
The HVS shall be subject to inspection by the Engineer of Record or the owner’s representative at either the place of manufacture or the project site. Any and all observed defects shall be repaired to the satisfaction of the owner or owner’s representative or replacement shall be made available.
C. Warranty
The manufacturer shall guarantee the HVS from defects in materials and workmanship for a period of two years following installation. If during the warranty period defects in materials or workmanship are noted, then the manufacturer shall be promptly notified. The decision to repair or replace affected units shall be made at the discretion of the manufacturer.
D. Patent Indemnity
Upon request, the manufacturer shall warrant that the HVS does not infringe upon or violate any patent, copyright, trade secret or any other proprietary right of any third party and shall indemnify the Owner against any loss, cost, expense or liability arising out of such claim whether or not such claim is successful.
E. Certificate of Compliance
Upon request, the manufacturer shall provide a “Letter of Certification” to certify that the HVS adheres to the specifications required herein and complies with the project’s stormwater management permit.
1.05 MANUFACTURER
A. The HVS shall be supplied by a manufacturer regularly engaged in such work who has furnished similar installations that have been in successful and continuous operation for a minimum period of five years. The manufacturer shall be a Stormwater Equipment Manufacturer Association (SWEMA) member.
B. The HVS shall be certified by an acceptable State agency, such as a State Department of Environmental Protection (DEP) or industry verification or assessment agency (e.g.: ETV, NJCAT, NETE).
PART 2 – STORMWATER HVS
2.01 GENERAL
A. The HVS shall use a tangential inlet pipe to establish rotational flow within a cylindrical vortex chamber or be able to treat the Water Quality Flow Rate stated herein without re-suspending and releasing captured pollutants. The HVS shall not release captured floating pollutants during surcharge conditions.
B. The HVS shall not exceed the pressure drop (headloss) for the design flow rates specified herein as determined by ASTM C1745 / C1745M – 11.
C. The HVS shall fit within the limits of excavation (area and depth) as shown in the project plans and will not exceed the dimensions for the design flow rates specified herein.
D. The storage capacities for pollutants that settle (sediment) and float (oil) shall not be less than the volumes listed in Table 1. The HVS shall operate as intended and perform as specified herein as pollutants accumulate. The storage capacity for pollutants that settle shall not reduce the volume required in the HVS for separation and for preventing re-suspension and washout, or reduce the floatables storage volume capacity.
E. Minimum 24-inch openings shall provide access to the sediment storage volumes from the surface for inspection and maintenance. Two access openings shall be provided for systems larger than 4 feet in diameter or 4 feet square. Removal of pollutants from the HVS shall be possible without requiring confined space entry.
2.02 PERFORMANCE
A. Performance of the HVS shall be based on independent full-scale laboratory and/or field testing and shall adhere to the Performance Specifications listed in Table 1. The laboratory testing used as the basis of product performance shall be undertaken in accordance with testing protocols approved or endorsed by SWEMA or acceptable State agency, such as a State Department of Environmental Protection (DEP) or recognized verification agency (e.g.: ETV, NJCAT, NETE).
B. Performance of the HVS shall be based on treating the Water Quality Flow rate (WQF) without internally bypassing and without re-suspension and washout of captured pollutants (scour). The Maximum Treatment Flow Rate(s) (MTFR-50 and/or MTFR-100) shall be greater than or equal to the WQF. The HVS shall remove greater than or equal to 80% of TSS based on the Target Particle Size (TPS) of 50 microns and/or 100 microns at MTFR-50 and MTFR-100, respectively.
C. The HVS shall treat all flows without internally bypassing up to the Peak Treatment Flow Rate (PTFR). Full-scale independent laboratory scour testing shall demonstrate effluent control of less than or equal to 20 mg/L for all flows up to 150% of MTFR-100 without internal or external bypass.
D. The HVS shall be capable of capturing and retaining fine silt and sand size particles. Analysis of captured sediment from full-scale field installations shall demonstrate particle sizes predominately in the 20-micron range.
E. The HVS shall capture and retain 100% of all floating trash and debris and remove greater than 80% of hydrocarbons up to its rated storage capacities under conditions of a catastrophic spill such as might be experienced in an automobile or truck accident spill like conditions.
Table 1 goes here (brings Spec Table from separate tab)
Notes:
1. Depth measurement is from the outlet invert to top of the bottom slab.
2. MTFR-50 and MTFR-100 are the Maximum Treatment Flow Rates for removing target particle sizes of 50 microns and 100 microns, respectively.
3. Scour Flow Rates are based on testing that demonstrates retention of captured sediment having a D50 of 100. Effluent concentrations shall not exceed 20 mg/L.
4. PTFR or Peak Treatment Flow Rate is based on the HVS maintaining positive removal efficiencies and headlosses no greater than those listed above for each model.
5. Headlosses are the difference in water elevations upstream and downstream of the HVS as determined by ASTM C1745 / C1745M – 11. The headlosses listed above for any particular model are for that HVS operating at the Peak Treatment Flow Rate.
6. Refer to 2.02 E.
PART 3 – EQUIPMENT
A. The HVS shall be manufactured with materials typically used in stormwater drainage systems that have a minimum life expectancy of 30 years.
(i) Materials of construction shall be cross-linked polyethylene (XLPE) and/or Type 304 stainless steel or carbon steel powder coated in accordance with ASTM 775/ ASTM A775M with a resulting thickness of 8-12 mils. All components shall be designed to withstand all normal loadings associated with fabrication, shipping, site installation, and normal operation of the equipment.
(ii) Precast shall be manufactured with concrete that has attained a compressive strength of 4,000 psi after 28 days. The structure shall be reinforced to withstand an HS20-44 loading. Shiplap joints shall be sealed with butyl rubber mastic sealant conforming to ASTM C990. Slab tops shall be suitably reinforced and provided with manhole openings and covers as required. The cast iron manhole frames and covers shall be sized as per the manufacturer’s drawings and shall be in accordance with ASTM A48, CL.35B and AASHTO M105. The masonry fixing bolts shall be Type 304 stainless steel.
(iii) All piping connections and ancillary items not listed herein shall be provided by the Contractor.
PART 4 - EQUIPMENT DELIVERY
A. The HVS components shall be delivered within six weeks of date of approved technical submittal.
B. The HVS components shall be preassembled and delivered to the site fully fabricated and ready for the final assembly.
C. Off-loading, storage, and installation shall be by the Contractor.
D. The Contractor shall inspect and provide signed acceptance of equipment prior to unloading, or notify the manufacturer of any damage to equipment to effect proper remedial action. Failure to notify the manufacturer of damage to equipment prior to unloading will void all warranties pertaining to subject equipment.
PART 5 - EQUIPMENT INSTALLATION
A. The system shall be installed in strict accordance with the site plans, and the manufacturer’s general arrangement drawings and Handling, Storage and Installation Instructions. The Contractor shall be responsible for installing the equipment and all necessary site connections.
B. The Manufacturer shall be notified immediately of any equipment which is damaged during unloading, storage, or installation. The damaged equipment shall be repaired or replaced at the discretion of the manufacturer and entirely at the Contractor’s expense.
C. The precast concrete structure shall be set on a granular or compacted sand sub-base in accordance with local requirements for standard manhole installation. In no instances shall the compacted sub-base material have a thickness of less than 12 inches.
D. The precast concrete structure shall be set level and plumb to within 0.5%.
E. Non-shrink grout or hydraulic cement conforming to ASTM C 595 shall be used to provide a water tight seal in the lift holes, any drain holes and around the concrete knock-outs for the inlet and outlet pipes.
F. The Contractor shall, at the discretion of the owner or owner’s representative, test the concrete structure for water tightness before backfilling.

## Performance (hidden)
Downstream Defender Performance Specifications
Flow Rate Parameters | Target Particle Size | Model Diameter (feet)
|  | 4 | 6 | 8 | 10 | 12
| Micron | Flow Rates (cfs)
Peak Treatment Flow Rates |  | 3 | 8 | 15 | 25 | 38
Water Quality Flow Rates (80% Removal) | 100 | 1.56 | 4.2989 | 8.8247 | 15.4161 | 24.318
| 50 | 1.2338 | 3.4 | 6.8795 | 12.0927 | 19.0333
Downstream Defender® Performance Specifications
[7 empty] | Model | Depth1 | MTFR-502 | MTFR-1003 | PTFR4 | Scour Flow Rate5 | Headloss6 | Oil Storage Capacity | Sediment Storage Capacity
[7 empty] | (feet) | (feet) | (cfs) | (cfs) | (cfs) | (cfs) | (feet) | (gal.) | (gal.)
[7 empty] | 4 | 4.08 | 1.2338 | 1.56 | 3 | 2.3588 | 0.68 | 70 | 141 | 4 | 12 | 2.8 | 4.08
[7 empty] | 6 | 5.86 | 3.4 | 4.2989 | 8 | 6.5 | 0.95 | 216 | 424 | 6 | 18 | 3.2 | 5.86
[7 empty] | 8 | 7.67 | 6.8795 | 8.8247 | 15 | 13.3432 | 1.1 | 540 | 939 | 8 | 24 | 4.2 | 7.67
[7 empty] | 10 | 9.44 | 12.0927 | 15.4161 | 25 | 23.3096 | 1.2 | 1050 | 1757 | 10 | 30 | 5 | 9.44
[7 empty] | 12 | 11.18 | 19.0333 | 24.318 | 38 | 36.7696 | 1.4 | 1770 | 2970 | 12 | 36 | 5.6 | 11.18

## 4-Get Specification
Get Downstream Defender Specification
| Click | this link | to download the latest version of the Downstream Defender Specification from our website.
Note: An Internet Connection is required to follow the link to the specification file.
Downstream Defender®
Sizing Calculator BETAv2.0

## 5-Submit For Free Design Review
Ready for a free Technical Design Review and Price Estimate?
Once you have calculculated the Downstream Defender model size needed, obtained a GA drawing and gotten a specificaiton,
click below to submit your DD Sizing Calculator *.xls file to Hydro International for a free design review and price estimate.
Click to go to Online Submission Form.
Downstream Defender®
Sizing Calculator For Projects Designed According to the Kansas City MARC Manual Sizing Method

## 6-Tell Us What You Think (hidden)
Your feedback is important to us.
The Downstream Defender Sizing Calculator BETA version was released so your valuable user feedback could be collected and incorporated
into the next version of the software.
Please help us improve the Downstream Defender Sizing Calculator by submitting your comments on our short, 6-question Feedback Form.
Thank You!
Tell Us What You Think
Go to Feedback Form