## Project
Updates and Contacts:
[12 empty] | This version is: | R3.31 | Check! | Email Spreadsheet Author:
| Project Name: | Project Name |  |  |  |  | Designer:
| Street: | Project Street |  |  |  |  | Company: |  |  |  |  | Tech Support: | techsupport@hydro-int.com |  |  | Phillip Taylor: | ptaylor@hydro-int.com
| City: | Project City |  |  |  |  | Office:
| State: | Project State |  |  |  |  | email:
| Country: | Project Country |  |  |  |  | Phone:
| Post Code: | Project Code
Treatment Parameters Help:
TREATMENT PARAMETERS | [5 empty] | Select Units: | US
"Minimum Particle Size" sets the particle size distribution from about 1000 µm down to the listed particle size.
| TSS Removal Goal: | 80 | % Removal |  |  |  | Trash Design Required? | Yes
| Minimum Particle Size: | 425 | µm |  |  |  | Select Mesh Size: | 19mm (0.75") Std |  |  | "Mesh Size" is should be 19 mm unless local regulations require the use of 5 mm screens.
| Water Quality Flow Rate: | 0 | cfs |  |  |  | Peak Design Flow: | 0 |  | cfs | "Peak Design Flow" is not used other than to provide a manual check and for information used in review.
STANDARD VAULT SIZES RESULTS | [10 empty] | Standard Vault Sizes Help:
Model Number | TSS % | Max. Pipe |  | Max. Treatment Capacity | [6 empty] | Standard vault size results displayed are updated with changes to the Treatment Parameters.
HDS4X8 | 100% | 32 in |  | 33.6 cfs | [6 empty] | Not all standard vault sizes may be availbale in all areas and local precast suppliers may produce different vault sizes. Use the Custom Vault Design option below if you need to use a locally avaible range of sizes.
HDS6X12 | 100% | 42 in |  | 66.4 cfs
HDS8X14 | 100% | 48 in |  | 92.7 cfs
HDS10X16 | 100% | 54 in |  | 124.4 cfs
HDS12X20 | 100% | 60 in |  | 161.9 cfs | [6 empty] | Custom Vault Sizes Help:
CUSTOMIZE VAULT DESIGN | [10 empty] | The Short Side Length is generally the inlet and outlet ends. The Long Side is the direction of the flow.
| Enter Short Side Length: | 0 | ft |  | Water Quality Result: | [5 empty] | #DIV/0!
| Enter Long Side Length: | 0 | ft |  | Model Number | TSS % | Max. Pipe | Max. Treatment Capacity
| Vault Area: | 0 | sq.ft | [7 empty] | Custom Design Side Length Limit Warnings:
| Model Number: | HDS0X0 |  |  | HDS0X0 | 100% | 20 in |  | 10.4 cfs
SELECTED VAULT AND SITE LAYOUT DETAILS | [10 empty] | Custom vaults are listed at the bottom of the "Select Vault" menu option.
Select Vault: | HDS4X8 |  |  |  |  | Structure ID: | Manhole1
Cover Required for Model Selected
| Installation: | New Development |  |  |  | Rim Level: | 100 | ft
| Placement: | Online |  |  |  | Inlet Invert: | 95 | ft |  |  | OK
| Inlet Pipe Size: | 48 | in | Max. 32in |  | Outlet Invert: | 95 | ft |  |  | OK
| Outlet Pipe Size: | 48 | in | Max. 32in
| Allowable Peak Flow: | 92.7003 | cfs | Limited by outlet pipe size.
(If Allowable Peak Flow is less than actual peak use an external bypass or increase outlet pipe size.)
NOTES:
4.00 ft
8.00 ft
24.44 in
62.44 in
95.000 ft
95.000 ft
24.44 in
Rim: 100.000 ft
Max. Treatment Flow Rate: 33.64 cfs
Min. Open Orifice Area of Screens: 26.13 sq.ft.
Min. Screenings Storage Capacity: 2.634 cu.yd.
Min. Sediment Storage Capacity: 2.414 cu.yd.
HYDRO DRYSCREEN MODEL HDS4X8 SPECIFICATION
1. MANHOLE WALL & SLAB THICKNESS NOT TO SCALE.
2. DRAWING NOT TO BE USED FOR CONSTRUCTION.
3. CONTACT HYDRO FOR MORE INFORMATION ON SPECIFIC PROJECT DESIGN & PRICING.
Hydro DryScreenTM
Water Quality Flow Rate Worksheet
TREATMENT UNIT HAS BEEN DESIGNED TO REMOVE A MIN. 80% TSS BASED ON A PSD RANGE DOWN TO A MIN. 425 µm AT A WATER QUALITY FLOW RATE OF 0 cfs
4 ft
Screen Mesh Size: 19mm (0.75") Std
Project Name
Project Street
Project City
Manhole1
Project State

## Change Log (hidden)
1 | Max pipe size - allow oversiing of pipes with limited peak flows? Is max. pipe currently set to equal the area of 80% of screen area.
2 | Custom Vault Designation
3 | Weir height and screen height relationship
4 | Peak flow calculation - make sure this is correctly calculated and how this is done.
5 | Buffering Sediment storage - what is this.
6
2017-08-02 | Changed from ActOn to CRM for version check | R3.31

## WQFCalc (hidden)
SLR Equations | [14 empty] | Find Vault Area given Flow and TSS%
| Removal to | [7 empty] | Drop Down Menu
| 425 | y=-0.0022x+1.1983 | [12 empty] | 425 | area=(%-1.1983)/(-0.0022*gpm)
| 300 | y=-0.0038x+1.1803 | [6 empty] | PSD |  | Model US | Model Metric |  |  | 300 | area=(%-1.1803)/(-0.0038*gpm)
| 212 | y=-0.0044x+1.0966 | [6 empty] | 106 |  | HDS4X8 | HDS1200x2400 |  |  | 212 | area=(%-1.0966)/(-0.0044*gpm)
| 150 | y=-0.0046x+1.0437 | [6 empty] | 150 |  | HDS6X12 | HDS1800x3600 |  |  | 150 | area=(%-1.0437)/(-0.0046*gpm)
| 106 | y=-0.0046x+1.0168 | [6 empty] | 212 |  | HDS8X14 | HDS2400x4200 |  |  | 106 | area=(%-1.0168)/(-0.0046*gpm)
| DryScreen | [7 empty] | 300 |  | HDS10X16 | HDS3600x4900 | [9 empty] | User Input Side Length
| Unit | width (ft) | length (ft) | Area (ft2) | SLR (gpm/ft2) |  |  |  | 425 |  | HDS12X20 | HDS3600x6100 |  |  | TSS: | 0.8 | [5 empty] | Short | Long
| 4x8 | 4 | 8 | 32 | 0 |  |  |  | Trash |  | HDS0X0 | Custom |  |  | TSS: | ft2 |  |  | ft |  |  | 0 | 0
| 6x12 | 6 | 12 | 72 | 0 | [9 empty] | 106 | 0 |  | Long Side Length: | #DIV/0! |  |  | Calc Long Side |  |  | Message
| 8x14 | 8 | 14 | 112 | 0 | [9 empty] | 150 | 0 |  | Long Side Length: | #DIV/0! |  |  | #DIV/0! | ft |  | #DIV/0!
| 10x16 | 10 | 16 | 160 | 0 | [9 empty] | 212 | 0 |  | Long Side Length: | #DIV/0!
| 12x20 | 12 | 20 | 240 | 0 | [9 empty] | 300 | 0 |  | Long Side Length: | #DIV/0!
| Custom | 0 | 0 | 0 | #DIV/0! | [9 empty] | 425 | 0 |  | Long Side Length: | #DIV/0!
[15 empty] | Trash | 0 |  | Long Side Length: | #DIV/0!
USER Inputs |  | 0 | [12 empty] | Metric
| WQF Input = | 0 | cfs | TSS: | 425 | [9 empty] | TSS: | m2 |  |  | m
|  | 0 | gpm | [11 empty] | 106 | 0 |  | Long Side Length: | #DIV/0!
[15 empty] | 150 | 0 |  | Long Side Length: | #DIV/0!
Down to Efficiency Calculations. | [14 empty] | 212 | 0 |  | Long Side Length: | #DIV/0!
SLR |  | 106 | 150 | 212 | 300 | 425 | Trash | [7 empty] | 300 | 0 |  | Long Side Length: | #DIV/0!
0 | HDS4X8 | 101.7% | 104.4% | 109.7% | 118% | 119.8% | N/A | [7 empty] | 425 | 0 |  | Long Side Length: | #DIV/0!
0 | HDS8X12 | 101.7% | 104.4% | 109.7% | 118% | 119.8% | N/A | [7 empty] | Trash | 0 |  | Long Side Length: | #DIV/0!
0 | HDS8X14 | 101.7% | 104.4% | 109.7% | 118% | 119.8% | N/A
0 | HDS10X16 | 101.7% | 104.4% | 109.7% | 118% | 119.8% | N/A | [7 empty] | Dimensions Checks and Max Size
0 | HDS12X20 | 101.7% | 104.4% | 109.7% | 118% | 119.8% | N/A |  | Custom Vault Eff | [5 empty] | Max Short Side: | 12 | ft |  | Check Messages
#DIV/0! | HDS4X8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A |  | #DIV/0! | 1 |  |  |  |  | User Input: | 0 | ft |  |  | Short side exceeds 12 ft. (3.66 m.) Reduce length or consult Hydro for options.
Long side exceeds 20 ft. (6.1 m.) Increase short side or consult Hydro for options.
[15 empty] | Max Long Side Length: | 20 | ft |  |  | Decrease short side length.
Reported Results | [14 empty] | User Input: | 0 | ft |  | Check Message Displayed:
User Selected |  |  | Actual | Rounded
PSD= | 425 | HDS4X8 | 119.8% | 100% | These are shown as the output
|  | HDS8X12 | 119.8% | 100% | These are shown as the output
|  | HDS8X14 | 119.8% | 100% | These are shown as the output
|  | HDS10X16 | 119.8% | 100% | These are shown as the output
|  | HDS12X20 | 119.8% | 100% | These are shown as the output
|  | HDS4X8 | 119.8% | 100% | These are shown as the output
User Selected Model
HDS4X8
Properties.
| Width | Length | Weir Ht. | Downstream Gap | Screen Height | Screen Area | Open Area | Max Pipe | Pipe Area | Allowed Blockage | Min Screen Storage Storage | Total Sediment Storage | Invert to Sump | Internal Height | Top Slab & Frame | Rim to Inv | Max Flow | Open Screen Area | Min Sediment Storage
| (feet) | (feet) | (feet) | (feet) | (feet) | (sq.ft.) | (sq.ft) | (in) | (sq.ft.) | % | (cu.yd.) | (cu.yd.) | (in) | (in) | (in) | (in) | (cfs) | (sq.ft) | (cu.yd.)
| 4 | 8 | 2.0369 | 1.3333 | 2.6667 | 37.3333 | 26.1333 | 32 | 5.5851 | 0.78629 | 2.634 | 2.4141 | 24.4428 | 62.4428 | 12 | 50 | 33.6398 | 26.1333 | 2.4141
| Width | Length | Weir Ht. | Downstream Gap | Screen Height | Screen Area | Open Area | Max Pipe | Pipe Area | Allowed Blockage | Min Screen Storage Storage | Total Sediment Storage | Invert to Sump | Internal Height | Top Slab & Frame | Rim to inv | Max Flow | Open Screen Area | Min Sediment Storage
Metric | (m) | (m) | (m) | (m) | (m) | (m2) | (m2) | (mm) | (m2) | % | (m3) | (m3) | (m) | (m) | (m) | (m) | (L/s) | (m2) | (m3)
| 1.219 | 2.438 | 0.621 | 0.406 | 0.813 | 3.468 | 7.965 | 813 | 0.51887 | 78.63% | 2.014 | 1.8457 | 0.621 | 1.586 | 0.305 | 1.27 | 952.57 | 2.428 | 1.846
Design Statement.
[29 empty] | User TSS: | 100 |  | TREATMENT UNIT HAS BEEN DESIGNED TO REMOVE A MIN. 80% TSS BASED ON A PSD RANGE DOWN TO A MIN. 425 µm AT A WATER QUALITY FLOW RATE OF 0 cfs
Drawing |  | Unit flag (US=1)= | 1 | DWG Text Boxes | [11 empty] | HYDRO DRYSCREEN MODEL |  |  |  | HDS4X8 |  | HYDRO DRYSCREEN MODEL HDS4X8 SPECIFICATION | [6 empty] | PSD: | 425 |  | TREATMENT UNIT HAS BEEN DESIGNED TO REMOVE TRASH AT A WATER QUALITY FLOW RATE OF 0 cfs
|  |  |  | width= | 4 | ft | 4.00 ft |  | Internal Height= |  | 62.4428 | in | 62.44 in |  |  | Max. Treatment Flow Rate: |  |  |  | 33.64 | cfs | Max. Treatment Flow Rate: 33.64 cfs | [6 empty] | WQf: | 0 | cfs
Project= | Project Name |  |  | length= | 8 | ft | 8.00 ft |  | Inlet Invert= |  | 95 | ft | 95.000 ft |  |  | Min. Open Orifice Area of Screens: |  |  |  | 26.13 | sq.ft. | Min. Open Orifice Area of Screens: 26.13 sq.ft. | [9 empty] | TREATMENT UNIT HAS BEEN DESIGNED TO REMOVE A MIN. 80% TSS BASED ON A PSD RANGE DOWN TO A MIN. 425 µm AT A WATER QUALITY FLOW RATE OF 0 cfs
Street= | Project Street |  |  | Invert to sump= | 24.4428 | in | 24.44 in |  | Outlet Invert= |  | 95 | ft | 95.000 ft |  |  | Min. Screenings Storage Capacity: |  |  |  | 2.634 | cu.yd. | Min. Screenings Storage Capacity: 2.634 cu.yd.
City= | Project City | [7 empty] | Rim Level= |  | 100 | ft | Rim: 100.000 ft |  |  | Min. Sediment Storage Capacity: |  |  |  | 2.414 | cu.yd. | Min. Sediment Storage Capacity: 2.414 cu.yd.
| Project State | [14 empty] | Screen Mesh Size: |  |  |  | 19mm (0.75") Std |  | Screen Mesh Size: 19mm (0.75") Std
Peak Flow and Arrangement Flags
Checks | [8 empty] | User | Min Cover | Actual Cover |  |  |  |  | Online | 92.7003 | Excess Peak Flow
|  | User | Allowable | Check |  |  |  | Rim= | 100
Inlet pipe size= |  | 48 | 32 | Max. 32in | in |  |  | inlet invert= | 95 | 4.167 | 5 | OK | ft
outlet pipe size= |  | 48 | 32 | Max. 32in | in |  |  | oulet invet= | 95 | 4.167 | 5 | OK | ft
This is used to determine the users specified pipe size bypass flow.
[22 empty] | Output Table Summary of Results | [7 empty] | Outlet Pipe Bypass Flow
Unit | Width | Length | Weir Ht. | Downstream Gap | Screen Height | Screen Area | Open Area | Max Pipe | Pipe Area | Allowed Blockage | Total Screen Storage | Total Sediment Storage | Invert to Sump | Min Internal Height | Top Slab & Frame | Min Rim to Inv | Max Bypass Flow | Max Treatment Capacity | Typical Treatment Flow |  |  |  | Max Pipe |  | Max Flow |  |  |  |  | User Outlet Pipe size | Pipe Area | Bypass Flow
| (feet) | (feet) | (feet) | (feet) | (feet) | (sq.ft.) | (sq.ft) | (in) | (sq.ft.) | % | (cu.yd.) | (cu.yd.) | (in) | (in) | (in) | (in) | (cfs) | (cfs) | (cfs) |  |  |  | (in) |  | (cfs) |  |  |  |  | 48 | 12.5664 | 92.7003 | cfs
HDS4X8 | 4 | 8 | 2.0369 | 1.3333 | 2.6667 | 37.3333 | 26.1333 | 32 | 5.5851 | 78.63% | 2.6337 | 2.4141 | 24.4428 | 62.4428 | 12 | 50 | 33.6398 | 23.5478 | 10.6944 |  |  |  | 32 | in | 33.6 | cfs | 32 in | 33.6 cfs |  |  |  | 2624.9802 | L/s
HDS6X12 | 6 | 12 | 3.2468 | 1.75 | 3.5 | 82.5 | 57.75 | 42 | 9.6211 | 83.34% | 7.9722 | 8.6581 | 38.9614 | 86.9614 | 14 | 62 | 66.3898 | 46.4729 | 24.0624 |  |  |  | 42 | in | 66.4 | cfs | 42 in | 66.4 cfs |  |  |  | 92.7003 | Value reported
HDS8X14 | 8 | 14 | 3.5925 | 2 | 4 | 128 | 89.6 | 48 | 12.5664 | 85.98% | 14.2222 | 14.9021 | 43.1096 | 97.1096 | 14 | 68 | 92.7003 | 64.8902 | 37.4304 |  |  |  | 48 | in | 92.7 | cfs | 48 in | 92.7 cfs
HDS10X16 | 10 | 16 | 3.7791 | 2.25 | 4.5 | 182.5 | 127.75 | 54 | 15.9043 | 87.55% | 22.9167 | 22.3949 | 45.3497 | 105.3497 | 16 | 76 | 124.4407 | 87.1085 | 53.472 |  |  |  | 54 | in | 124.4 | cfs | 54 in | 124.4 cfs
HDS12X20 | 12 | 20 | 3.9243 | 2.5 | 5 | 270 | 189 | 60 | 19.635 | 89.61% | 38.8889 | 34.8829 | 47.0919 | 113.0919 | 16 | 82 | 161.9408 | 113.3585 | 80.208 |  |  |  | 60 | in | 161.9 | cfs | 60 in | 161.9 cfs
HDS0X0 | 0 | 0 | #DIV/0! | 0.83333 | 1.6667 | 0 | 0 | 20 | 2.1817 | #DIV/0! | 0 | -2.5811 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 10.3885 | 7.272 | 0 |  |  |  | 20 | in | 10.4 | cfs | 20 in | 10.4 cfs
| Width | Length | Weir Ht. | Downstream Gap | Screen Height | Screen Area | Open Area | Max Pipe | Pipe Area | Allowed Blockage | Total Screen Storage | Total Sediment Storage | Invert to Sump | Min Internal Height | Top Slab & Frame | Min Rim to Inv | Max Bypass Flow | [5 empty] | Max Pipe |  | Max Flow
Metric | (m) | (m) | (m) | (m) | (m) | (m2) | (m2) | (mm) | (m2) | % | (m3) | (m3) | (m) | (m) | (m) | (m) | (L/s) | [5 empty] | (mm) |  | (L/s)
HDS4X8 | 1.2192 | 2.4384 | 0.62085 | 0.4064 | 0.8128 | 3.4684 | 7.9654 | 812.8 | 0.51887 | 78.63% | 2.0136 | 1.8457 | 0.62085 | 1.586 | 0.3048 | 1.27 | 952.5722 | [5 empty] | 813 | mm | 953 | L/s | 813 mm | 953 L/s
HDS6X12 | 1.8288 | 3.6576 | 0.98962 | 0.5334 | 1.0668 | 7.6645 | 17.6022 | 1066.8 | 0.89383 | 83.34% | 6.0952 | 6.6196 | 0.98962 | 2.2088 | 0.3556 | 1.5748 | 1879.9495 | [5 empty] | 1067 | mm | 1880 | L/s | 1067 mm | 1880 L/s
HDS8X14 | 2.4384 | 4.2672 | 1.095 | 0.6096 | 1.2192 | 11.8916 | 27.3101 | 1219.2 | 1.1675 | 85.98% | 10.8737 | 11.3935 | 1.095 | 2.4666 | 0.3556 | 1.7272 | 2624.9802 | [5 empty] | 1219 | mm | 2625 | L/s | 1219 mm | 2625 L/s
HDS10X16 | 3.048 | 4.8768 | 1.1519 | 0.6858 | 1.3716 | 16.9548 | 38.9382 | 1371.6 | 1.4776 | 87.55% | 17.521 | 17.1221 | 1.1519 | 2.6759 | 0.4064 | 1.9304 | 3523.7683 | [5 empty] | 1372 | mm | 3524 | L/s | 1372 mm | 3524 L/s
HDS12X20 | 3.6576 | 6.096 | 1.1961 | 0.762 | 1.524 | 25.0838 | 57.6072 | 1524 | 1.8241 | 89.61% | 29.7327 | 26.6699 | 1.1961 | 2.8725 | 0.4064 | 2.0828 | 4585.6518 | [5 empty] | 1524 | mm | 4586 | L/s | 1524 mm | 4586 L/s
HDS0X0 | 0 | 0 | #DIV/0! | 0.254 | 0.508 | 0 | 0 | 508 | 0.20268 | #DIV/0! | 0 | -1.9734 | #DIV/0! | #DIV/0! | 0.254 | #DIV/0! | 294.1697 | [5 empty] | 508 | mm | 294 | L/s | 508 mm | 294 L/s
Jeremy Fink Table
|  |  |  | Downstream | Screen |  |  | Max | Pipe | Allowed | Total Screen | Total Sediment |  | Invert | Min Int. | Top Slab | Min Rim | Bypass | Max. Treat | Typ. Treat
Suntree | Width | Length | Weir Ht. | Gap | Height | Screen Area | Open Area | Pipe | Area | Blockage | Storage | Storage | Unit Area | to Sump | Height | & Frame | to Inv. | Flow | Capacity | Flow
Size | (feet) | (feet) | (feet) | (feet) | (feet) | (sq.ft.) | (sq.ft) | (in) | (sq.ft.) | % | (cu.yd.) | (cu.yd.) | (sq.ft) | (inch) | (inch) | (inch) | (in) | (cfs) | (cfs) | (cfs)
4x8 | 4 | 8 | 3 | 1.25 | 2.5 | 37 | 25.9 | 30 | 4.9087 | 81.05% | 2.5 | 3.5556 | 32 | 36 | 84 | 12 | 60 | 28.6274 | 22 | 10.6944
6x12 | 6 | 12 | 3 | 1.75 | 3.5 | 82.5 | 57.75 | 42 | 9.6211 | 83.34% | 7.9722 | 8 | 72 | 36 | 84 | 14 | 62 | 66.3898 | 46 | 24.0624
8x14 | 8 | 14 | 3.3333 | 2 | 4 | 128 | 89.6 | 48 | 12.5664 | 85.98% | 14.2222 | 13.8272 | 112 | 40 | 100 | 14 | 74 | 92.7003 | 65 | 37.4304
10x16 | 10 | 16 | 3.8333 | 2.25 | 4.5 | 182.5 | 127.75 | 54 | 15.9043 | 87.55% | 22.9167 | 22.716 | 160 | 46 | 125 | 16 | 95 | 124.4407 | 87 | 53.472
12x24 | 12 | 24 | 4 | 2.5 | 5 | 318 | 222.6 | 60 | 19.635 | 91.18% | 47.7778 | 42.6667 | 288 | 48 | 125 | 16 | 93 | 161.9408 | 113 | 96.2496
Screen Height Calculation.
| H=((Q/Cd*A)^2)/2g |  |  | User Inputs
|  |  |  | Q | Pipe | Pipe Area | g | H | Half pipe | Inv to Top of water | Bottom of Screen | TOS |  | Unit | Invert to TOS / TOP |  |  | Calculated Water Level
| H = Centerline of pipe |  |  | 92.7003 | 48 | 12.5664 | 32.2 | 2 | 2 | 4 | 0.3 | 4.3 |  |  | ft | m
| Q= Flow | [12 empty] | DS4X8 | 2.5 | 0.762 |  | 4 | ft | 4 ft
| Cd = 0.65 | [12 empty] | DS6X12 | 3.5 | 1.0668 |  | 4 | ft | 4 ft
| A = Pipe Area | [12 empty] | DS8X14 | 4 | 1.2192 |  | 4 | ft | 4 ft
[14 empty] | DS10X16 | 4.5 | 1.3716 |  | 4 | ft | 4 ft
[14 empty] | DS12X20 | 5 | 1.524 |  | 4 | ft | 4 ft
Top Slab to Smallest span relationship
|  |  | S | T
|  | HDS4X8 | 4 | 12
|  | HDS6X12 | 6 | 14
|  | HDS8X14 | 8 | 14
|  | HDS10X16 | 10 | 16
|  | HDS12X20 | 12 | 16
Note on D74: Jeremy B. Fink: See interpolated relationship below
Note on O74: Jeremy B. Fink: Weir Height + 3 inches for screen assy + Vert. Screen Height + 3 inches clearance
Note on P74: Jeremy B. Fink: From Precaster
Note on T74: Jeremy B. Fink: 150 gpm/sq.ft.

## Specification
Double Click To Open.
Specification
Brochure

## Links
Hydro International Links:
Contact Hydro:

## UserManual
Double clik to open

## FUTURE UPDATE TASKS (hidden)
1 | Rim to invert clearance check
2 | Links Page
3 | ReadMe page
4 | Specification
5 | User manual
6 | Standards detail drawing sheet, showing garde rings, DD and FD connections, onsite assembly notes, etc. Things that sould be on the construction set.
7
8
9
10
11
12
13
14
15
16
17
18
19